## ID-Serial
ArrayID | XML | HEX | Description | Decimal |  | Notes | Ref HEX | j3 | <- Enter Cell reference here to select required HEX string below
0 | STX | 02 | Start Transmission |  |  |  | j3 |  | 0200FE0648010B0A0D01FFFF191205040001FFFFFFFFFF0403FF01FFFFFFFFFFFFFFFFFFFFFFFF3134333131313032393932323020202043616C656E74612020202020202020200319120525A30104160EE614424D08920115230109780304020E2C1437502855
1 | HEADER | 00 | STRING SENT: Str1 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x14 0x99 0x04 0x03, Str2 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x15 0x58 0xC4 0x03 Str3 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x16 0x18 0xC5 0x03, Str4 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x17 0xD9 0x05 0x03 Str5 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x18 0x99 0x01 0x03, Str6 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x19 0x58 0xC1 0x03 Str7 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1A 0x18 0xC0 0x03, Str8 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1B 0xD9 0x00 0x03 |  |  |  | j3 |  | 0200FE0648010B0A0D01FFFF191205040001FFFFFFFFFF0403FF01FFFFFFFFFFFFFFFFFFFFFFFF3134333131313032393932323020202043616C656E74612020202020202020200319120525B70104160EE614424D089201152301097D0304020E2C1437502855
2 |  | FE |  |  |  |  | j3
3 |  | 06 |  |  |  |  | j3
4 |  | 48 |  |  |  |  | j3
5 |  | 01 |  |  |  |  | j3
6 |  | 0B |  |  |  |  | j3
7 | 0 | 0A |  | 10 |  |  | j3
8 | 1 | 0D | dF-Code (decimal) | 13 |  |  | j3
9 | 2 | 01 | dU-Code (decimal) | 1 |  |  | j3
10 | 3 | FF |  | 255 |  |  | j3
11 | 4 | FF |  | 255 |  |  | j3
12 | 5 | 19 | Software Version (hex/10 = 1.9) | 25 |  |  | j3
13 | 6 | 12 | Parameter Version (hex/10 = 1.2) | 18 |  |  | j3
14 | 7 | 05 | Parameter Type (hex) | 5 |  |  | j3
15 | 8 | 04 |  | 4 |  |  | j3
16 | 9 | 00 |  | 0 |  |  | j3
17 | 10 | 01 |  | 1 |  |  | j3
18 | 11 | FF |  | 255 |  |  | j3
19 | 12 | FF |  | 255 |  |  | j3
20 | 13 | FF |  | 255 |  |  | j3
21 | 14 | FF |  | 255 |  |  | j3
22 | 15 | FF |  | 255 |  |  | j3
23 | 16 | 04 |  | 4 |  |  | j3
24 | 17 | 03 |  | 3 |  |  | j3
25 | 18 | FF |  | 255 |  |  | j3
26 | 19 | 01 |  | 1 |  |  | j3
27 | 20 | FF |  | 255 |  |  | j3
28 | 21 | FF |  | 255 |  |  | j3
29 | 22 | FF |  | 255 |  |  | j3
30 | 23 | FF |  | 255 |  |  | j3
31 | 24 | FF |  | 255 |  |  | j3
32 | 25 | FF |  | 255 |  |  | j3
33 | 26 | FF |  | 255 |  |  | j3
34 | 27 | FF |  | 255 |  |  | j3
35 | 28 | FF |  | 255 |  |  | j3
36 | 29 | FF |  | 255 |  |  | j3
37 | 30 | FF |  | 255 |  |  | j3
38 | 31 | FF |  | 255 |  |  | j3
39 | 32 | 31 | Boiler Serial 1431110299220 (concat ASCII) | 49 | 1 |  | j3
40 | 33 | 34 |  | 52 | 4 |  | j3
41 | 34 | 33 |  | 51 | 3 |  | j3
42 | 35 | 31 |  | 49 | 1 |  | j3
43 | 36 | 31 |  | 49 | 1 |  | j3
44 | 37 | 31 |  | 49 | 1 |  | j3
45 | 38 | 30 |  | 48 | 0 |  | j3
46 | 39 | 32 |  | 50 | 2 |  | j3
47 | 40 | 39 |  | 57 | 9 |  | j3
48 | 41 | 39 |  | 57 | 9 |  | j3
49 | 42 | 32 |  | 50 | 2 |  | j3
50 | 43 | 32 |  | 50 | 2 |  | j3
51 | 44 | 30 |  | 48 | 0 |  | j3
52 | 45 | 20 |  | 32 |  |  | j3
53 | 46 | 20 |  | 32 |  |  | j3
54 | 47 | 20 |  | 32 |  |  | j3
55 | 48 | 43 | Boiler Name = Calenta (concat ASCII) | 67 | C |  | j3
56 | 49 | 61 |  | 97 | a |  | j3
57 | 50 | 6C |  | 108 | l |  | j3
58 | 51 | 65 |  | 101 | e |  | j3
59 | 52 | 6E |  | 110 | n |  | j3
60 | 53 | 74 |  | 116 | t |  | j3
61 | 54 | 61 |  | 97 | a |  | j3
62 | 55 | 20 |  | 32 |  |  | j3
63 | 56 | 20 |  | 32 |  |  | j3
64 | 57 | 20 |  | 32 |  |  | j3
65 | 58 | 20 |  | 32 |  |  | j3
66 | 59 | 20 |  | 32 |  |  | j3
67 | 60 | 20 |  | 32 |  |  | j3
68 | 61 | 20 |  | 32 |  |  | j3
69 | 62 | 20 |  | 32 |  |  | j3
70 | 63 | 20 |  | 32 |  |  | j3
71 | 64 | 03 | PCU - Device Type (hex) | 3 |  |  | j3
72 | 65 | 19 | PCU - Software Version (hex/10 = 1.9) | 25 |  |  | j3
73 | 66 | 12 | PCU - Parameter Version (hex/10 = 1.2) | 18 |  |  | j3
74 | 67 | 05 | PCU - Parameter Type (hex) | 5 |  |  | j3
75 | 68 | 25 | Operating Hours ( =((E77*256)+E78)*2) | 37 | 19310 |  | j3
76 | 69 | B7 |  | 183 |  |  | j3
77 | 70 | 01 | PCU - Connected SU Type | 1 |  |  | j3
78 | 71 | 04 | PCU - Connected PSU Type | 4 |  |  | j3
79 | 72 | 16 | PCU - Last blocking code (decimal) | 22 |  |  | j3
80 | 73 | 0E | PCU - Last locking code (decimal) | 14 |  |  | j3
81 | 74 | E6 | PCU - Operating voltage (decimal) | 230 |  |  | j3
82 | 75 | 14 | Serial = 1442M0892 |  |  |  | j3
83 | 76 | 42 |  |  |  |  | j3
84 | 77 | 4D |  | 77 | M |  | j3
85 | 78 | 08 |  |  |  |  | j3
86 | 79 | 92 |  |  |  |  | j3
87 | 80 | 01 | Device Type (decimal) | 1 |  |  | j3
88 | 81 | 15 | Software Version (hex/10 = 1.5) |  |  |  | j3
89 | 82 | 23 | Parameter Version (hex/10 = 2.3) |  |  |  | j3
90 | 83 | 01 | Parameter Type (decimal) | 1 |  |  | j3
91 | 84 | 09 |  | 9 | 19432 |  | j3
92 | 85 | 7D |  | 125 |  |  | j3
93 | 86 | 03 | SU no. 1 - Connected PCU Type | 3 | connected PCU type |  | j3
94 | 87 | 04 | SU no. 1 - Connected PSU Type | 4 | Connected PSU type |  | j3
95 | 88 | 02 | SU no. 1 - Last blocking code | 2 | last blocking code |  | j3
96 | 89 | 0E | SU no. 1 - Last locking code | 14 | Last locking code |  | j3
97 | 90 | 2C | SU no. 1 - Last internal error | 44 | Last internal error |  | j3
98 | 91 | 14 | SU no. 1 Serial Number (concat) |  | 14 |  | j3
99 | 92 | 37 |  |  | 37 |  | j3
100 | 93 | 50 |  | 80 | P |  | j3
101 | 94 | 28 |  |  | 28 |  | j3
102 | 95 | 55 |  |  | 55 |  | j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
|  |  | Send: |  |  | Response

## Samples
ArrayID | XML | HEX | Description | Hex2Dec | Decimal | Notes | Ref HEX | j27 | <- Enter Cell reference here to select required HEX string below
0 | STX | 02 | Start Transmission |  |  |  | j27 |  | 0201fe06480201cd0ccd090080008080f3008004103408800c70173408ef06ef063c800c0014006400000003c6405503ffff1e000004ffff1000020b000000008000000000000014b603
1 | HEADER | 01 | STRING SENT: 0x02 0xFE 0x01 0x05 0x08 0x02 0x01 0x69 0xAB 0x03 |  |  |  | j27 |  | 0201fe06480201ff15aa100080008080f30080d8113408441670173408620962095044161914006419000003c6401503ffff1e000004ffff130082160000000080000000000000cfd403
2 |  | FE |  |  |  |  | j27 |  | 0201fe064802010b16a9100080008080f30080da113408441670173408730972095144161a1400641a000003c6401503ffff1e000004ffff130078160000000080000000000000c89703
3 |  | 06 |  |  |  |  | j27 |  | 0201fe06480201fc159c100080008080f30080da113408e01570173408a308a9084fe0151114006412000003c6401503ffff1e000004ffff1300701600000000800000000000009a3e03
4 |  | 48 |  |  |  |  | j27 |  | 0201fe064802016c1591100080008080f30080da113408e01570173408c708c7084de0151314006413000003c6401503ffff1e000004ffff13005d160000000080000000000000221603
5 |  | 02 |  |  |  |  | j27 |  | 0201fe06480201791590100080008080f30080d3113408e01570173408e808e7084de0151414006414000003c6401503ffff1e000004ffff13004a160000000080000000000000393803
6 |  | 01 |  |  |  |  | j27 |  | 0201fe064802019d1584100080008080f30080da113408e01570173408180918094ee0151614006416000003c6401503ffff1e000004ffff13002b160000000080000000000000784e03
7 | 0 | FF | Flow Temp | 255 | 38.39 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27 |  | 0201fe06480201aa1584100080008080f30080da113408e01570173408290928094fe0151714006417000003c6401503ffff1e000004ffff130020160000000080000000000000cf4703
8 | 1 | 0E |  | 14 |  |  | j27 |  | 0201fe064802017d1578100080008080f30080da1134087c1570173408590859084c7c150e1400640e000003c6401503ffff1e000004ffff130016160000000080000000000000c5ea03
9 | 2 | 0B | Return Temp | 11 | 23.15 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27 |  | 0201fe06480201ff146d100080008080f30080da1134087c1570173408850884084a7c151014006410000003c6401503ffff1e000004ffff1300021600000000800000000000007b1e03
10 | 3 | 09 |  | 9 |  |  | j27 |  | 0201fe064802010f1561100080008080f30080da1134087c1570173408a708a7084a7c151214006412000003c6401503ffff1e000004ffff1300ed150000000080000000000000397903
11 | 4 | 00 | DHW-in Temperature | 0 | 0 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27 |  | 0201fe06480201241560100080008080f30080da1134087c1570173408c108c1084a7c151314006413000003c6401503ffff1e000004ffff1300dc150000000080000000000000090103
12 | 5 | 80 |  | 128 |  |  | j27 |  | 0201fe06480201e61460100080008080f30080da113408181570173408680868084918150f1400640f000003c6401503ffff1e000004ffff1300cb15000000008000000000000056f203
13 | 6 | 00 | Outside Temp | 0 | 0 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27 |  | 0201fe06480201c1175f130080008080f300803610d00764197017340816082c085570170536006406000083ce585104ffff25000004ffff12006f170f02000080000000000000941803
14 | 7 | 80 |  | 128 |  |  | j27 |  | 0201fe06480201ff1623130080008080f300804010d0076419701734080f080a084570170523006405000083ce585104ffff1e000004ffff12003717ea01000080000000000000b0f203
15 | 8 | 80 | Calorifier Temperature | 128 | -32 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27 |  | 0201fe06480201601783120080008080f300804a10d0076419701734083d083b084570170614006406000083ce585104ffff1e000004ffff12004917f701000080000000000000127903
16 | 9 | F3 |  | 243 |  |  | j27 |  | 0201fe06480201851779120080008080f300805c10d007641970173408670869084870170714006407000083ce585104ffff1e000004ffff12005617fa01000080000000000000a9ab03
17 | 10 | 00 |  |  |  | --- NOT IN USE --- | j27 |  | 0201fe0648020190178c120080008080f300806810d00764197017340860085d084870170714006407000083ce585104ffff1e000004ffff12006617fa010000800000000000002df703
18 | 11 | 80 |  |  |  | --- NOT IN USE --- | j27 |  | 0201fe0648020191178e120080008080f300807c10d0076419701734086e086c084870170714006407000083ce585104ffff1e000004ffff12006717f901000080000000000000019e03
19 | 12 | 68 | Boiler Control Temp B | 104 | 42 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27 |  | 0201fe06480201981790120080008080f300808610d007641970173408650863084870170714006407000083ce585104ffff1e000004ffff12006c17fa010000800000000000009d3e03
20 | 13 | 10 |  | 16 |  |  | j27 |  | 0201fe064802019c1791120080008080f30080a410d0076419701734085e0860084870170714006407000083ce585104ffff1e000004ffff12006e17f501000080000000000000618303
21 | 14 | 34 | Room Temp B | 52 | 21 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27 |  | 0201fe06480201c21778120080008080f30080b810d007641970173408a408a7084b70170814006408000083ce585104ffff1e000004ffff1200751709020000800000000000004a9403
22 | 15 | 08 |  | 8 |  |  | j27 |  | 0201fe06480201711753110080008080f30080c210d007641970173408cf0bb30b5728233521006432000003c6401503ffff25000004ffff1300b80f000000008000000000000026f403
23 | 16 | A0 | CH Setpoint B | 160 | 40 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27 |  | 0201FE06480201D914CE120080008080F30080AA0FFA07BC027C15D0070000000000BC020000006400000001C20B1000FFFF00000000FFFF1000BC0200000000800000000000000EE003
24 | 17 | 0F |  | 15 |  |  | j27 |  | 0201FE06480201A9127F120080008080F3008086103408BC027C15D0070000000000BC020000006400000001C20B1000FFFF00000000FFFF1000BC0200000000800000000000004A7903
25 | 18 | 7C | DHW Setpoint B | 124 | 55 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27 |  | 0201FE06480201FF0E0B090080008080F3008068103408A00F7C153408F109F20955A00F1F1400641F000003C6401503FFFF1E000004FFFF1000810D0000000080000000000000F95703
26 | 19 | 15 |  | 21 |  |  | j27
27 | 20 | 34 | Room Temp setpoint Opentherm B | 52 | 21 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27
28 | 21 | 08 |  | 8 |  |  | j27
29 | 22 | F1 | Fan Speed setpoint B | 241 | 2545 | A.0+B.1 = (A*256)+B | j27
30 | 23 | 09 |  | 9 |  |  | j27
31 | 24 | F2 | Fan Speed B | 242 | 2546 | A.0+B.1 = (A*256)+B | j27
32 | 25 | 09 |  | 9 |  |  | j27
33 | 26 | 55 | Ionisation Current | 85 | 8.5 | A*0.1 | j27
34 | 27 | A0 | Internal Setpoint B | 160 | 40 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27
35 | 28 | 0F |  | 15 |  |  | j27
36 | 29 | 1F | Available Power (Output) | 31 | 31 | A | j27
37 | 30 | 14 | Pump Percentage (Speed) | 20 | 20 | A | j27
38 | 31 | 00 |  |  |  | --- NOT IN USE --- | j27
39 | 32 | 64 | Desired Max Power (Required Output) | 100 | 100 | A | j27
40 | 33 | 1F | Actual Power from boiler | 31 | 31 | A | j27
41 | 34 | 00 |  |  |  | --- NOT IN USE --- | j27
42 | 35 | 00 |  |  |  | --- NOT IN USE --- | j27
43 | 36 | 03 | Various BIT Settings (Demand Source) | 3 | 00000011 | BIT0=Mod.Controller Connected, BIT1=Heat demand from Mod.Controller, BIT2=Heat demand from on/off controller, BIT3=Frost Protection, BIT4=DHW Eco, BIT5=DHW Blocking, BIT6=Anti Legionella, BIT7=DHW Heat Demand | j27
44 | 37 | C6 | Various BIT Settings (Input) | 198 | 11000110 | BIT0=Shudown Input, BIT1=Release Input, BIT2=Ionisation, BIT3=Flow Switch detecting DHW, BIT5=Min Gas Pressure, BIT6=CH Enable, BIT7=DHW Enable | j27
45 | 38 | 40 | Various BIT Settings (Valve) | 64 | 01000000 | BIT0=Gas Valve, BIT2=Ignition, BIT3=3-Way valve position, BIT4=Ext.3-Way Valve, BIT6=Ext. Gas Valve | j27
46 | 39 | 15 | Various BIT Settings (Pump) | 21 | 00010101 | BIT0=Pump, BIT1=Calorifier Pump, BIT2=Ext.CH Pump, BIT4=Status Report, BIT7=Opentherm SmartPower | j27
47 | 40 | 03 | State | 3 | 3 | 3:Burning CH | j27
48 | 41 | FF | Lockout E | 255 | 255 | No locking | j27
49 | 42 | FF | Blocking b | 255 | 255 | No blocking | j27
50 | 43 | 1E | Sub-State | 30 | 30 | 30:Normal internal setpoint | j27
51 | 44 | 00 |  |  |  | --- NOT IN USE --- | j27
52 | 45 | 00 |  |  |  | --- NOT IN USE --- | j27
53 | 46 | 04 |  |  |  | --- NOT IN USE --- | j27
54 | 47 | FF |  |  |  | --- NOT IN USE --- | j27
55 | 48 | FF |  |  |  | --- NOT IN USE --- | j27
56 | 49 | 10 | Hydro. Pressure | 16 | 1.6 | System water pressure | j27
57 | 50 | 00 | HRU | 0 | 00000000 | BIT1=HRU Active | j27
58 | 51 | 81 | Control Temp A | 129 | 34.57 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27
59 | 52 | 0D |  | 13 |  |  | j27
60 | 53 | 00 | DHW Flowrate A | 0 | 0 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27
61 | 54 | 00 |  | 0 |  |  | j27
62 | 55 | 00 |  |  |  | --- NOT IN USE --- | j27
63 | 56 | 00 | Solar Temp A | 0 | 0 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j27
64 | 57 | 80 |  | 128 |  |  | j27
65 | 58 | 00 |  |  |  | --- NOT IN USE --- | j27
66 | 59 | 00 |  |  |  | --- NOT IN USE --- | j27
67 | 60 | 00 |  |  |  | --- NOT IN USE --- | j27
68 | 61 | 00 |  |  |  | --- NOT IN USE --- | j27
69 | 62 | 00 |  |  |  | --- NOT IN USE --- | j27
70 | 63 | 00 |  |  |  | --- NOT IN USE --- | j27
71 | 64 | F9 | CRC |  |  | CRC | j27
72 | 65 | 57 |  |  |  |  | j27
73 | 66 | 03 | End Transmission |  |  |  | j27
State - Lookup |  |  |  | Lockout - Lookup
0 | 0:Standby |  |  | 0 | PSU not connected (Locking 0)
1 | 1:Boiler start |  |  | 1 | SU parameter fault (Locking 1)
2 | 2:Burner start |  |  | 2 | 02:T Flow closed
3 | 3:Burning CH |  |  | 3 | 03:T Flow open
4 | 4:Burning DHW |  |  | 4 | 04:T Flow < min.
5 | 5:Burner stop |  |  | 5 | 05:T Flow > max.
6 | 6:Boiler stop |  |  | 6 | T Return closed (Locking 6)
7 | 7:- |  |  | 7 | T Return open (Locking 7)
8 | 8:Controlled stop |  |  | 8 | T Return < min. (Locking 8)
9 | 9:Blocking mode |  |  | 9 | T Return > max. (Locking 9)
10 | 10:Locking mode |  |  | 10 | 10:dT(Flow,Return) > max.
11 | 11:Chimney mode L |  |  | 11 | 11:dT(Return,Flow) > max.
12 | 12:Chimney mode h |  |  | 12 | STB activated (Locking 12)
13 | 13:Chimney mode H |  |  | 14 | 5x Unsuccessful start (Locking 14)
14 | 14:- |  |  | 16 | False flame (Locking 16)
15 | 15:Manual-heatdemand |  |  | 17 | SU Gasvalve driver error (Locking 17)
16 | 16:Boiler-frost-protection |  |  | 34 | Fan out of control range (Locking 34)
17 | 17:De-airation |  |  | 35 | Return over Flow temp. (Locking 35)
999 | Unknown State |  |  | 36 | 5x Flame loss (Locking 36)
|  |  |  | 37 | SU communication (Locking 37)
Sub-Status |  |  |  | 38 | SCU-S communication (Locking 38)
0 | 0:Standby |  |  | 39 | BL input as lockout (Locking 39)
1 | 1:Anti-cycling |  |  | 40 | - (Locking 40)
2 | 2:Open hydraulic valve |  |  | 255 | No locking
3 | 3:Pump start |  |  | 999 | Unknown locking code
4 | 4:Wait for burner start
10 | 10:Open external gas valve |  |  | Blocking - Lookup
11 | 11:Fan to fluegasvalve speed |  |  | 0 | PCU parameter fault (Blocking 0)
12 | 12:Open fluegasvalve |  |  | 1 | T Flow > max.(Blocking 1)
13 | 13:Pre-purge |  |  | 2 | dT/s Flow > max. (Blocking 2)
14 | 14:Wait for release |  |  | 7 | dT(Flow,Return) > max.(Blocking 7)
15 | 15:Burner start |  |  | 8 | No release signal(Blocking 8)
16 | 16:VPS test |  |  | 9 | L-N swept(Blocking 9)
17 | 17:Pre-ignition |  |  | 10 | Blocking signal ex frost(Blocking 10)
18 | 18:Ignition |  |  | 11 | Blocking signal inc frost(Blocking 11)
19 | 19:Flame check |  |  | 13 | SCU communication(Blocking 13)
20 | 20:Interpurge |  |  | 14 | Min. water pressure(Blocking 14)
30 | 30:Normal internal setpoint |  |  | 15 | Min. gas pressure(Blocking 15)
31 | 31:Limited internal setpoint |  |  | 16 | Ident. SU mismatch(Blocking 16)
32 | 32:Normal power control |  |  | 17 | Ident. dF/dU table error(Blocking 17)
33 | 33:Gradient control level 1 |  |  | 18 | Ident. PSU mismatch(Blocking 18)
34 | 34:Gradient control level 2 |  |  | 19 | Ident. dF/dU needed(Blocking 19)
35 | 35:Gradient control level 3 |  |  | 20 | Identification running(Blocking 20)
36 | 36:Flame protection |  |  | 21 | SU communications lost(Blocking 21)
37 | 37:Stabilization time |  |  | 22 | Flame lost(Blocking 22)
38 | 38:Cold start |  |  | 25 | Internal SU error(Blocking 25)
39 | 39:Limited power Tfg |  |  | 26 | Calorifier sensor error(Blocking 26)
40 | 40:Burner stop |  |  | 27 | DHW in sensor error(Blocking 27)
41 | 41:Post purge |  |  | 255 | No blocking
42 | 42:Fan to fluegasvalve speed |  |  | 999 | Unknown blocking code
43 | 43:Close fluegasvalve
44 | 44:Stop fan
45 | 45:Close external gas valve
60 | 60:Pump post running
61 | 61:Pump stop
62 | 62:Close hydraulic valve
63 | 63:Start anti-cycle timer
255 | 255:Reset wait time
999 | Unknown Sub-State

## Counters
ArrayID | XML | HEX | Description | Hex2Dec | Decimal | Notes |  | Resp1-1C | Resp2-1D | Resp3-1E | Resp4-1F
0 | STX | 2 | Start Transmission |  |  |  | START | 2 | 2 | 2 | 2
1 | HEADER | 0 | STRING SENT: Str1 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1C 0x98 0xC2 0x03 Str2 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1D 0x59 0x02 0x03 Str3 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1E 0x19 0x03 0x03 Str4 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1F 0xD8 0xC3 0x03 |  |  |  | HEADER | 0 | 0 | 0 | 0
2 |  | FE | [5 empty] | FE | FE | FE | FE
3 |  | 6 | [5 empty] | 6 | 6 | 6 | 6
4 |  | 18 | [5 empty] | 18 | 18 | 18 | 18
5 |  | 10 | [5 empty] | 10 | 10 | 10 | 10
6 |  | 1C | [5 empty] | 1C | 1D | 1E | 1F
7 | 0 | 3 | Hours run pump CH+DHW | 3 | 1844 | (A.1+B.0)*2 | 0 | 3 | 9 | 0 | 0
8 |  | 9a |  | 154 |  |  | 1 | 9A | A8 | 0 | 0
9 | 2 | 21 | Hours run 3-way valve DHW | 33 | 17072 | (A.1+B.0)*2 | 2 | 21 | 0 | 0 | 0
10 |  | 58 |  | 88 |  |  | 3 | 56 | 4 | 0 | 0
11 | 4 | 2 | Hours run CH+DHW | 2 | 1436 | (A.1+B.0)*2 | 4 | 2 | 0 | 0 | 0
12 |  | ce |  | 206 |  |  | 5 | CE | 2 | 0 | 0
13 | 6 | 0 | Hours run DHW | 0 | 60 | (A.1+B.0) | 6 | 0 | 0 | 0 | 0
14 |  | 3c |  | 60 |  |  | 7 | 3C | 0 | 0 | 0
15 | 8 | 24 | Power Supply available hours | 36 | 18700 | (A.1+B.0)*2 | 8 | 24 | 0 | 0 | 0
16 |  | 86 |  | 134 |  |  | 9 | 84 | 0 | 0 | 0
17 | 10 | 0 | Pump starts CH+DHW | 0 | 320 | (A.1+B.0)*8 | 10 | 0 | 0 | 0 | 0
18 |  | 28 |  | 40 |  |  | 11 | 27 | 0 | 0 | 0
19 | 12 | 1 | Number of 3-Way valve cycles | 1 | 2096 | (A.1+B.0)*8 | 12 | 1 | 0 | 0 | 0
20 |  | 6 |  | 6 |  |  | 13 | 6 | 0 | 0 | 0
21 | 14 | 8 | Burner Starts DHW A | 8 | 17952 | (A.1+B.0)*8 | 14 | 8 | 0 | 0 | 0
22 |  | c4 |  | 196 |  |  | 15 | C4 | 0 | 0 | 0
23 | 16 | 9 | Total Burner Starts CH+DHW A | 9 | 19776 | (A.1+B.0)*8 | CRC | A4 | 8 | 93 | C2
24 |  | A8 |  | 168 |  |  | CRC | 57 | 99 | 7D | ED
25 | 18 | 0 | Failed burner starts A | 0 | 4 | (A.1+B.0) | END | 3 | 3 | 3 | 3
26 |  | 4 |  | 4
27 | 20 | 0 | Number of flame loss A | 0 | 2 | (A.1+B.0)
28 |  | 2 |  | 2
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | ** Note** | Looks like only Str1 and Str2 are needed - others return NULL

## Parameters
ArrayID | XML | HEX | Description | Decimal | Notes | Ref HEX | I2 | <- Enter Cell reference here to select required HEX string below
0 | STX | 02 | Start Transmission |  |  | I2 |  | 0200FE06181014413C010200020501FFFFFFFFFFFFFFFF2A44114B28085AFF1414F10206F60014040000010100000100000001AF1E23FFFFFFFFFFFFFFFFFFFFFFC802002313220128465A3219051E0A1E0309444428145039075405000F02050632190001B3090078640A061E284B00FE0A000A6402281A010A05021428141E7A0A00FF000C1A
1 | HEADER | 00 | STRING SENT: Str1 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x14 0x99 0x04 0x03, Str2 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x15 0x58 0xC4 0x03 Str3 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x16 0x18 0xC5 0x03, Str4 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x17 0xD9 0x05 0x03 Str5 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x18 0x99 0x01 0x03, Str6 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x19 0x58 0xC1 0x03 Str7 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1A 0x18 0xC0 0x03, Str8 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1B 0xD9 0x00 0x03 |  |  | I2
2 |  | FE |  |  |  | I2
3 |  | 06 |  |  |  | I2
4 |  | 18 |  |  |  | I2
5 |  | 10 |  |  |  | I2
6 |  | 14 |  |  |  | I2
7 | 0 | 41 | Max flow temperature during CH mode | 65 | °C | I2
8 | 1 | 3C | Desired DHW temperature | 60 | °C | I2
9 | 2 | 01 | Switch on/off CH/DHW function | 1 | 0:CH Off DHW Off; 1:CH On DHW On; 2:CH On DHW Off; 3:CH Off DHW On | I2
10 | 3 | 02 | Comfort DHW | 2 | 0: Always On; 1:Always Off; 2:Controller | I2
11 | 4 | 00 | Anticipation current on/off thermostat | 0 | 0:No; 1:Yes | I2
12 | 5 | 02 | Amount of information on display | 2 | 0:Simple; 1:Extended; 2:Automatic; 3:Automatic+Key Lock | I2
13 | 6 | 05 | Pump Post Run time | 5 | minutes | I2
14 | 7 | 01 | Display brightness when backlight active | 1 | 0:Low; 1:Bright | I2
15 | 8 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
16 | 9 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
17 | 10 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
18 | 11 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
19 | 12 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
20 | 13 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
21 | 14 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
22 | 15 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
23 | 16 | 2A | Max fanspeed during CH mode | 4200 | A x 100 RPM | I2
24 | 17 | 44 | Max fanspeed during DHW mode | 6800 | A x 100 RPM | I2
25 | 18 | 11 | Max fanspeed during CH+DHW mode | 1700 | A x 100 RPM | I2
26 | 19 | 4B | Offset on partload fanspeed | 75 | RPM | I2
27 | 20 | 28 | Fan speed at boiler start | 4000 | A x 100 RPM | I2
28 | 21 | 08 | Minimum waterpressure for notification | 0.8 | A x 0.1 bar | I2
29 | 22 | 5A | Maximum flow temperature for heating system | 90 | °C | I2
30 | 23 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
31 | 24 | 14 | Footpoint heating curve outside temperature | 20 | °C | I2
32 | 25 | 14 | Footpoint heating curve flow temperature | 20 | °C | I2
33 | 26 | F1 | Clima point heating curve outside temperature | -15 | SGN(A) °C - [Signed 8bit] | I2
34 | 27 | 02 | Pump CH Min | 20 | A x 10% (2) | I2
35 | 28 | 06 | Pump CH Max | 60 | A x 10% (6) | I2
36 | 29 | F6 | Minimum outside temperature for frost protection | -10 | SGN(A) °C - [Signed 8bit] | I2
37 | 30 | 00 | Legionella Protection | 0 | 0:No; 1:Yes; 2:Controller | I2
38 | 31 | 14 | Setpoint raise at warming up calorifier | 20 | °C | I2
39 | 32 | 04 | Switch on hystereses calorifier sensor | 4 | °C | I2
40 | 33 | 00 | 3-Way valve standby: CH or DHW | 0 | 0:CH, 1:DHW | I2
41 | 34 | 00 | Boiler type | 0 | 0:Combi ; 1:Solo(+boiler); 2:Comfort Column | I2
42 | 35 | 01 | Function of blocking input | 1 | 0:CH enable; 1:Blocking without frost protection; 2:Blocking with frost protection; 3:Locking with frost protection | I2
43 | 36 | 01 | Function of release input | 1 | 0:DHW enable; 1:Burner release | I2
44 | 37 | 00 | Wait time for valid release signal, 0=no check | 0 | seconds | I2
45 | 38 | 00 | Wait time for fluegas valve | 0 | seconds | I2
46 | 39 | 01 | Position from alarm/operation signal relay | 1 | 0:Operation Signal; 1:Failure signal | I2
47 | 40 | 00 | Min gas pressure detection | 0 | 0:No; 1:Yes | I2
48 | 41 | 00 | HRU connected | 0 | 0:No; 1:Yes | I2
49 | 42 | 00 | Mains L-N phase detection activated | 0 | 0:No; 1:Yes | I2
50 | 43 | 01 | Service Notification for boiler dependant maint. | 1 | 0:Off; 1:ABC; 2:Custom | I2
51 | 44 | AF | Service Hours for boiler connected to mains supply | 17500 | A x 100 hours (17500h = ~729 days = ~2 years) [175] | I2
52 | 45 | 1E | Service Hours for boiler burner | 3000 | A x 100 hours 3000h = ~125 days but not based on 24hours/day) [30] | I2
53 | 46 | 23 | Tau factor for average flow temperature calculation | 35 | seconds | I2
54 | 47 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
55 | 48 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
56 | 49 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
57 | 50 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
58 | 51 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
59 | 52 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
60 | 53 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
61 | 54 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
62 | 55 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
63 | 56 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
64 | 57 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
65 | 58 | C8 | DHW-in gradient for restart stabilisation time | 2 | 0.01 °C/second | I2
66 | 59 | 02 | dT pump offset | 2 | °C | I2
67 | 60 | 00 | Offset control temp | 0 | SGN(A) /10 °C [Signed 8bit] | I2
68 | 61 | 23 | DHW Flow at minimum output power | 3.5 | A x 0.1 litres/minute | I2
69 | 62 | 13 | --- NOT IN USE --- | 19 | --- NOT IN USE --- | I2
70 | 63 | 22 | --- NOT IN USE --- | 34 | --- NOT IN USE --- | I2
71 | 64 | 01 | Number of de-airation cycles on startup | 1 |  | I2
72 | 65 | 28 | Maximum gradient for decreasing modulation | 0.4 | 0.01 °C/second | I2
73 | 66 | 46 | Maximum gradient for forced minimal load | 0.7 | 0.01 °C/second | I2
74 | 67 | 5A | Maximum gradient for blocking | 0.9 | 0.01 °C/second | I2
75 | 68 | 32 | Maximum temperature difference between flow & return | 50 | °C | I2
76 | 69 | 19 | Modulate back when dT > this par | 25 | °C | I2
77 | 70 | 05 | Pump control range dT for CH | 5 | °C | I2
78 | 71 | 1E | Pump control CH on start heat demand | 30 | % | I2
79 | 72 | 0A | Start hysteresis for CH | 10 | °C | I2
80 | 73 | 1E | Stabilisation time after burner start CH | 30 | seconds | I2
81 | 74 | 03 | Minimum burner anti-cycle time | 3 | minutes | I2
82 | 75 | 09 | Maximum burner anti-cycle time | 9 | minutes | I2
83 | 76 | 44 | Absolute maximum fan speed CH | 6800 | A x 100 RPM | I2
84 | 77 | 44 | Absolute maximum fan speed DHW | 6800 | A x 100 RPM | I2
85 | 78 | 28 | Pump control, control range dT for DHW | 40 | °C | I2
86 | 79 | 14 | Pump control, DHW minimum speed | 20 | % | I2
87 | 80 | 50 | Pump control, DHW maximum speed | 80 | % | I2
88 | 81 | 39 | Pump control, DHW on start DHW demand | 57 | % | I2
89 | 82 | 07 | Warm up interval for DHW after CH | 7 | minutes | I2
90 | 83 | 54 | Time between warming up starts boiler | 84 | minutes | I2
91 | 84 | 05 | Hysterese when warming up for DHW comfort | 5 | °C | I2
92 | 85 | 00 | Offset when warming up for DHW comfort | 0 | SGN(A) °C - [Signed 8bit] | I2
93 | 86 | 0F | DHW start raise depending on DHW flow | 15 |  | I2
94 | 87 | 02 | Switch on hystereses DHW operation | 2 | °C | I2
95 | 88 | 05 | Offset DHW | 5 | °C | I2
96 | 89 | 06 | T correction DHW for Tset, ww - Tret, plate heat exchanger | 6 | °C | I2
97 | 90 | 32 | %Tf/Tr for DHW control temp at pumpspeed 20% | 50 | % | I2
98 | 91 | 19 | %Tf/Tr for DHW control temp at pumpspeed 100% | 25 | % | I2
99 | 92 | 00 | Waiting time pump for preheat plate heat exchanger | 0 | per 10 seconds | I2
100 | 93 | 01 | Postpump time DHW | 1 | seconds | I2
101 | 94 | B3 | Correction factor DHW pulses to l/min | 179 | per second | I2
102 | 95 | 09 | Min DHW flow for DHW detection | 0.9 | A x 0.1 litres/minute | I2
103 | 96 | 00 | Type of sensor for DHW detection | 0 | 0:DHW flow sensor; 1:DHW flow switch | I2
104 | 97 | 78 | Factor for dynamic flow detection | 120 |  | I2
105 | 98 | 64 | DHW stabilisation time for pump modulation | 10 | /10 seconds | I2
106 | 99 | 0A | DHW gradient for stabilisation time pump | 0.1 | 0.01 °C/second | I2
107 | 100 | 06 | Range in which the DHW booster is disabled | 6 | °C | I2
108 | 101 | 1E | P-Factor for booster on start DHW | 30 |  | I2
109 | 102 | 28 | P-Factor for feedforward on flow DHW | 40 |  | I2
110 | 103 | 4B | P-Factor for booster on flow changes DHW | 75 |  | I2
111 | 104 | 00 | Switch off offset calorifier sensor | 0 | °C | I2
112 | 105 | FE | Switch on delay DHW pump in comparison with boiler pump | -2 | SGN(A) °C - [Signed 8bit] | I2
113 | 106 | 0A | Post pump time DHW | 10 | seconds | I2
114 | 107 | 00 | Pre-purge time for burner start | 0 | seconds | I2
115 | 108 | 0A | Post-purge time for burner stop | 10 | seconds | I2
116 | 109 | 64 | Maximum flow temperature for blocking | 100 | °C | I2
117 | 110 | 02 | Tacho pulses per revolution of the fan | 2 | per second | I2
118 | 111 | 28 | P-factor fan speed control | 40 |  | I2
119 | 112 | 1A | I-factor fan speed control | 26 |  | I2
120 | 113 | 01 | P-factor CH control | 1 |  | I2
121 | 114 | 0A | I-factor CH control | 10 |  | I2
122 | 115 | 05 | P-factor for CH control when T1>setpoint | 5 |  | I2
123 | 116 | 02 | I-factor for CH control when T1>setpoint | 2 |  | I2
124 | 117 | 14 | P-factor DHW control | 20 |  | I2
125 | 118 | 28 | I-factor DHW control | 40 |  | I2
126 | 119 | 14 | I-factor for pump control on CH | 20 |  | I2
127 | 120 | 1E | I-factor for pump control on DHW | 30 |  | I2
128 | 121 | 7A | RPM at theoreteical 0KW | 122 |  | I2
129 | 122 | 0A | Power output (KW) at theoretical 10,000RPM | 10 |  | I2
130 | 123 | 00 | PWM value red for normal display backlight | 0 | Think this will allow change to display colour based on RGB colours (e.g. 0000FF=Blue, FF0000=Red, FF00FF=Magenta, 800000=Maroon, 800080=Purple, etc. | I2
131 | 124 | FF | PWM value blue for normal display backlight | 255 |  | I2
132 | 125 | 00 | PWM value green for normal display backlight | 0 |  | I2
133 | 126 | 0C | --- NOT IN USE --- | 12 | --- NOT IN USE --- | I2
134 | 127 | 1A | --- NOT IN USE --- | 26 | --- NOT IN USE --- | I2
|  |  | Send: |  | Response
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x14 0x99 0x04 0x03 |  | 0200FE06181014413C010200020501FFFFFFFFFFFFFFFF299103
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x15 0x58 0xC4 0x03 |  | 0200FE061810152A44114B28085AFF1414F10206F600143E6603
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x16 0x18 0xC5 0x03 |  | 0200FE06181016040000010100000100000001AF1E23FFC10C03
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x17 0xD9 0x05 0x03 |  | 0200FE06181017FFFFFFFFFFFFFFFFFFFFC8020023132211BB03
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x18 0x99 0x01 0x03 |  | 0200FE061810180128465A3219051E0A1E030944442814BC4303
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x19 0x58 0xC1 0x03 |  | 0200FE061810195039075405000F02050632190001B309523403
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x1A 0x18 0xC0 0x03 |  | 0200FE0618101A0078640A061E284B00FE0A000A640228227F03
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x1B 0xD9 0x00 0x03 |  | 0200FE0618101B1A010A05021428141E7A0A00FF000C1AE4CD03

## Parameters-org
ArrayID | XML | HEX | Description | Decimal | Notes |  | Resp1-14 | Resp2-15 | Resp3-16 | Resp4-17 | Resp5-18 | Resp6-19 | Resp7-1A | Resp8-1B
0 | STX | 2 | Start Transmission |  |  | START | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
1 | HEADER | 0 | STRING SENT: Str1 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x14 0x99 0x04 0x03, Str2 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x15 0x58 0xC4 0x03 Str3 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x16 0x18 0xC5 0x03, Str4 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x17 0xD9 0x05 0x03 Str5 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x18 0x99 0x01 0x03, Str6 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x19 0x58 0xC1 0x03 Str7 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1A 0x18 0xC0 0x03, Str8 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1B 0xD9 0x00 0x03 |  |  | HEADER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 |  | fe | bar: Resp1-14 to Resp8-1B
3 |  | 6 |  |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
4 |  | 18 |  |  |  |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
5 |  | 10 |  |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
6 |  | 14 |  |  |  |  | 14 | 15 | 16 | 17 | 18 | 19 | 1a | 1b
7 | 0 | 41 | Max flow temperature during CH mode | 65 | °C | 0 | 41 | 2a | 4 | ff | 1 | 50 | 0 | 1a
8 | 1 | 3c | Desired DHW temperature | 60 | °C | 1 | 3c | 44 | 0 | ff | 28 | 39 | 78 | 1
9 | 2 | 1 | Switch on/off CH/DHW function | 1 | 0:CH Off DHW Off; 1:CH On DHW On; 2:CH On DHW Off; 3:CH Off DHW On | 2 | 1 | 11 | 0 | ff | 46 | 7 | 64 | 0a
10 | 3 | 2 | Comfort DHW | 2 | 0: Always On; 1:Always Off; 2:Controller | 3 | 2 | 4b | 1 | ff | 5a | 54 | 0a | 5
11 | 4 | 0 | Anticipation current on/off thermostat | 0 | 0:No; 1:Yes | 4 | 0 | 28 | 1 | ff | 32 | 5 | 6 | 2
12 | 5 | 2 | Amount of information on display | 2 | 0:Simple; 1:Extended; 2:Automatic; 3:Automatic+Key Lock | 5 | 2 | 8 | 0 | ff | 19 | 0 | 1e | 14
13 | 6 | 5 | Pump Post Run time | 5 | minutes | 6 | 5 | 5a | 0 | ff | 5 | 0f | 28 | 28
14 | 7 | 1 | Display brightness when backlight active | 1 | 0:Low; 1:Bright | 7 | 1 | ff | 1 | ff | 1e | 2 | 4b | 14
15 | 8 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 8 | ff | 14 | 0 | ff | 0a | 5 | 0 | 1e
16 | 9 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 9 | ff | 14 | 0 | ff | 1e | 6 | fe | 7a
17 | 10 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 10 | ff | f1 | 0 | c8 | 3 | 32 | 0a | 0a
18 | 11 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 11 | ff | 2 | 1 | 2 | 9 | 19 | 0 | 0
19 | 12 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 12 | ff | 6 | af | 0 | 44 | 0 | 0a | ff
20 | 13 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 13 | ff | f6 | 1e | 23 | 44 | 1 | 64 | 0
21 | 14 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 14 | ff | 0 | 23 | 13 | 28 | b3 | 2 | 0c
22 | 15 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 15 | ff | 14 | ff | 22 | 14 | 9 | 28 | 1a
23 | 16 | 2a | Max fanspeed during CH mode | 4200 | A x 100 RPM | CRC | 29 | 3e | c1 | 11 | bc | 52 | 22 | e4
24 | 17 | 44 | Max fanspeed during DHW mode | 6800 | A x 100 RPM | CRC | 91 | 66 | 0c | bb | 43 | 34 | 7f | cd
25 | 18 | 11 | Max fanspeed during CH+DHW mode | 1700 | A x 100 RPM | END | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
26 | 19 | 4b | Offset on partload fanspeed | 75 | RPM
27 | 20 | 28 | Fan speed at boiler start | 4000 | A x 100 RPM
28 | 21 | 8 | Minimum waterpressure for notification | 0.8 | A x 0.1 bar
29 | 22 | 5a | Maximum flow temperature for heating system | 90 | °C
30 | 23 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
31 | 24 | 14 | Footpoint heating curve outside temperature | 20 | °C
32 | 25 | 14 | Footpoint heating curve flow temperature | 20 | °C
33 | 26 | f1 | Clima point heating curve outside temperature | -15 | SGN(A) °C - [Signed 8bit]
34 | 27 | 2 | Pump CH Min | 20 | A x 10%
35 | 28 | 6 | Pump CH Max | 60 | A x 10%
36 | 29 | f6 | Minimum outside temperature for frost protection | -10 | SGN(A) °C - [Signed 8bit]
37 | 30 | 0 | Legionella Protection | 0 | 0:No; 1:Yes; 2:Controller
38 | 31 | 14 | Setpoint raise at warming up calorifier | 20 | °C
39 | 32 | 4 | Switch on hystereses calorifier sensor | 4 | °C
40 | 33 | 0 | 3-Way valve standby: CH or DHW | 0 | 0:CH, 1:DHW
41 | 34 | 0 | Boiler type | 0 | 0:Combi ; 1:Solo(+boiler); 2:Comfort Column
42 | 35 | 1 | Function of blocking input | 1 | 0:CH enable; 1:Blocking without frost protection; 2:Blocking with frost protection; 3:Locking with frost protection
43 | 36 | 1 | Function of release input | 1 | 0:DHW enable; 1:Burner release
44 | 37 | 0 | Wait time for valid release signal, 0=no check | 0 | seconds
45 | 38 | 0 | Wait time for fluegas valve | 0 | seconds
46 | 39 | 1 | Position from alarm/operation signal relay | 1 | 0:Operation Signal; 1:Failure signal
47 | 40 | 0 | Min gas pressure detection | 0 | 0:No; 1:Yes
48 | 41 | 0 | HRU connected | 0 | 0:No; 1:Yes
49 | 42 | 0 | Mains L-N phase detection activated | 0 | 0:No; 1:Yes
50 | 43 | 1 | Service Notification for boiler dependant maint. | 1 | 0:Off; 1:ABC; 2:Custom
51 | 44 | af | Service Hours for boiler connected to mains supply | 17500 | A x 100 hours (17500h = ~729 days = ~2 years)
52 | 45 | 1e | Service Hours for boiler burner | 3000 | A x 100 hours 3000h = ~125 days but not based on 24hours/day)
53 | 46 | 23 | Tau factor for average flow temperature calculation | 35 | seconds
54 | 47 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
55 | 48 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
56 | 49 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
57 | 50 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
58 | 51 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
59 | 52 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
60 | 53 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
61 | 54 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
62 | 55 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
63 | 56 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
64 | 57 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
65 | 58 | c8 | DHW-in gradient for restart stabilisation time | 2 | 0.01 °C/second
66 | 59 | 2 | dT pump offset | 2 | °C
67 | 60 | 0 | Offset control temp | 0 | SGN(A) /10 °C [Signed 8bit]
68 | 61 | 23 | DHW Flow at minimum output power | 3.5 | A x 0.1 litres/minute
69 | 62 | 13 | --- NOT IN USE --- | 19 | --- NOT IN USE ---
70 | 63 | 22 | --- NOT IN USE --- | 34 | --- NOT IN USE ---
71 | 64 | 1 | Number of de-airation cycles on startup | 1
72 | 65 | 28 | Maximum gradient for decreasing modulation | 0.4 | 0.01 °C/second
73 | 66 | 46 | Maximum gradient for forced minimal load | 0.7 | 0.01 °C/second
74 | 67 | 5a | Maximum gradient for blocking | 0.9 | 0.01 °C/second
75 | 68 | 32 | Maximum temperature difference between flow & return | 50 | °C
76 | 69 | 19 | Modulate back when dT > this par | 25 | °C
77 | 70 | 5 | Pump control range dT for CH | 5 | °C
78 | 71 | 1e | Pump control CH on start heat demand | 30 | %
79 | 72 | 0a | Start hysteresis for CH | 10 | °C
80 | 73 | 1e | Stabilisation time after burner start CH | 30 | seconds
81 | 74 | 3 | Minimum burner anti-cycle time | 3 | minutes
82 | 75 | 9 | Maximum burner anti-cycle time | 9 | minutes
83 | 76 | 44 | Absolute maximum fan speed CH | 6800 | A x 100 RPM
84 | 77 | 44 | Absolute maximum fan speed DHW | 6800 | A x 100 RPM
85 | 78 | 28 | Pump control, control range dT for DHW | 40 | °C
86 | 79 | 14 | Pump control, DHW minimum speed | 20 | %
87 | 80 | 50 | Pump control, DHW maximum speed | 80 | %
88 | 81 | 39 | Pump control, DHW on start DHW demand | 57 | %
89 | 82 | 7 | Warm up interval for DHW after CH | 7 | minutes
90 | 83 | 54 | Time between warming up starts boiler | 84 | minutes
91 | 84 | 5 | Hysterese when warming up for DHW comfort | 5 | °C
92 | 85 | 0 | Offset when warming up for DHW comfort | 0 | SGN(A) °C - [Signed 8bit]
93 | 86 | 0f | DHW start raise depending on DHW flow | 15
94 | 87 | 2 | Switch on hystereses DHW operation | 2 | °C
95 | 88 | 5 | Offset DHW | 5 | °C
96 | 89 | 6 | T correction DHW for Tset, ww - Tret, plate heat exchanger | 6 | °C
97 | 90 | 32 | %Tf/Tr for DHW control temp at pumpspeed 20% | 50 | %
98 | 91 | 19 | %Tf/Tr for DHW control temp at pumpspeed 100% | 25 | %
99 | 92 | 0 | Waiting time pump for preheat plate heat exchanger | 0 | per 10 seconds
100 | 93 | 1 | Postpump time DHW | 1 | seconds
101 | 94 | b3 | Correction factor DHW pulses to l/min | 179 | per second
102 | 95 | 9 | Min DHW flow for DHW detection | 0.9 | A x 0.1 litres/minute
103 | 96 | 0 | Type of sensor for DHW detection | 0 | 0:DHW flow sensor; 1:DHW flow switch
104 | 97 | 78 | Factor for dynamic flow detection | 120
105 | 98 | 64 | DHW stabilisation time for pump modulation | 10 | /10 seconds
106 | 99 | 0a | DHW gradient for stabilisation time pump | 0.1 | 0.01 °C/second
107 | 100 | 6 | Range in which the DHW booster is disabled | 6 | °C
108 | 101 | 1e | P-Factor for booster on start DHW | 30
109 | 102 | 28 | P-Factor for feedforward on flow DHW | 40
110 | 103 | 4b | P-Factor for booster on flow changes DHW | 75
111 | 104 | 0 | Switch off offset calorifier sensor | 0 | °C
112 | 105 | fe | Switch on delay DHW pump in comparison with boiler pump | -2 | SGN(A) °C - [Signed 8bit]
113 | 106 | 0a | Post pump time DHW | 10 | seconds
114 | 107 | 0 | Pre-purge time for burner start | 0 | seconds
115 | 108 | 0a | Post-purge time for burner stop | 10 | seconds
116 | 109 | 64 | Maximum flow temperature for blocking | 100 | °C
117 | 110 | 2 | Tacho pulses per revolution of the fan | 2 | per second
118 | 111 | 28 | P-factor fan speed control | 40
119 | 112 | 1a | I-factor fan speed control | 26
120 | 113 | 1 | P-factor CH control | 1
121 | 114 | 0a | I-factor CH control | 10
122 | 115 | 5 | P-factor for CH control when T1>setpoint | 5
123 | 116 | 2 | I-factor for CH control when T1>setpoint | 2
124 | 117 | 14 | P-factor DHW control | 20
125 | 118 | 28 | I-factor DHW control | 40
126 | 119 | 14 | I-factor for pump control on CH | 20
127 | 120 | 1e | I-factor for pump control on DHW | 30
128 | 121 | 7a | RPM at theoreteical 0KW | 122
129 | 122 | 0a | Power output (KW) at theoretical 10,000RPM | 10
130 | 123 | 0 | PWM value red for normal display backlight | 0 | Think this will allow change to display colour based on RGB colours (e.g. 0000FF=Blue, FF0000=Red, FF00FF=Magenta, 800000=Maroon, 800080=Purple, etc.
131 | 124 | ff | PWM value blue for normal display backlight | 255
132 | 125 | 0 | PWM value green for normal display backlight | 0
133 | 126 | 0c | --- NOT IN USE --- | 12 | --- NOT IN USE ---
134 | 127 | 1a | --- NOT IN USE --- | 26 | --- NOT IN USE ---
|  |  | Send: |  | Response
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x14 0x99 0x04 0x03 |  | 0200fe06181014413c010200020501ffffffffffffffff299103
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x15 0x58 0xC4 0x03 |  | 0200fe061810152a44114b28085aff1414f10206f600143e6603
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x16 0x18 0xC5 0x03 |  | 0200fe06181016040000010100000100000001af1e23ffc10c03
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x17 0xD9 0x05 0x03 |  | 0200fe06181017ffffffffffffffffffffc8020023132211bb03
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x18 0x99 0x01 0x03 |  | 0200fe061810180128465a3219051e0a1e030944442814bc4303
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x19 0x58 0xC1 0x03 |  | 0200fe061810195039075405000f02050632190001b309523403
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x1A 0x18 0xC0 0x03 |  | 0200fe0618101a0078640a061e284b00fe0a000a640228227f03
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x1B 0xD9 0x00 0x03 |  | 0200fe0618101b1a010a05021428141e7a0a00ff000c1ae4cd03

## Sheet1
Type | Group | Name | Description | Byte | Number | expression | Format
field | 1 | dF-code | dF-code | 1 |  | A | 0
field | 1 | dU-code | dU-code | 2 |  | A | 0
field | 1 | Software version | Software version | 5 | 6
field | 1 | Parameter version | Parameter version | 6 | 6
field | 1 | Parameter type | Parameter type | 7 |  | A | 0
select | 1 | Next Service code | Next Service code | 10 |  | A | 0
field | 1 | Serial number | Serial number | 32 | 4
field | 1 | Boiler name | Boiler name | 48 | 4
field | 2 | Device type | Device type | 0 |  | A | 0
field | 2 | Software version | Software version | 1 | 6
field | 2 | Parameter version | Parameter version | 2 | 6
field | 2 | Parameter type | Parameter type | 3 |  | A | 0
field | 2 | Operating hours | Operating hours | 4 |  | (A.1 + B.0) x 2 | 0
field | 2 | Connected SU type | Connected SU type | 6 |  | A | 0
field | 2 | Connected PSU type | Connected PSU type | 7 |  | A | 0
field | 2 | Last blocking code | Last blocking code | 8 |  | A | 0
field | 2 | Last locking code | Last locking code | 9 |  | A | 0
field | 2 | Operating Voltage | Operating Voltage | 10 |  | A | 0
field | 2 | Serial number | Serial number | 11 | 5
field | 3 | Device type | Device type | 0 |  | A | 0
field | 3 | Software version | Software version | 1 | 6
field | 3 | Parameter version | Parameter version | 2 | 6
field | 3 | Parameter type | Parameter type | 3 |  | A | 0
field | 3 | Operating hours | Operating hours | 4 |  | (A.1 + B.0) x 8 | 0
field | 3 | Connected PCU type | Connected PCU type | 6 |  | A | 0
field | 3 | Connected PSU type | Connected PSU type | 7 |  | A | 0
field | 3 | Last blocking code | Last blocking code | 8 |  | A | 0
field | 3 | Last locking code | Last locking code | 9 |  | A | 0
field | 3 | Last internal error | Last internal error | 10 |  | A | 0
field | 3 | Serial number | Serial number | 11 | 5
field | 4 | Device type | Device type | 0 |  | A | 0
field | 4 | Software version | Software version | 1 | 6
field | 4 | Operating hours | Operating hours | 4 |  | (A.1 + B.0) x 8 | 0
field | 4 | Serial number | Serial number | 11 | 5